## Slide 1: HOW TO SIZE A TANKLESS
It’s easier than you think!

## Slide 2
HOW TO SIZE A TANKLESS
Proper sizing is a key aspect of the customers experience and satisfaction with their tankless.
An undersized tankless will provide the proper temperature but the customer will not be able to run as many hot water fixtures at the same time as they want.
This problem will be more apparent in the winter time as the cold water temperatures are even colder.

## Slide 3
STEP ONE
Determine your maximum temperature rise. This is the difference between the tankless set temp. and the winter time ground water temp.
For the purpose of this example let’s say the home is on the central coast of California.
Based on the map, we’ll say the winter ground water temp is 55 F.
Now you can determine the winter time temperature rise:
120 Set Temp
– 55 Ground Water Temp
= 65
Average Winter Water Temp:
35° - 40° F
45° - 50° F
55° - 60° F
65° - 70°+ F

## Slide 4
STEP TWO
Determine the peak hot water demand of the home. If possible, ask the homeowner.
Shower: 2 gpm
Lav Sink: 1 gpm
Kitchen Sink: 1.5 gpm
Dishwasher: 2 gpm
Washing Machine: 2 gpm
Fixtures and appliances all have different flow rates depending on manufacturer however you can use an average amount to get a ballpark figure:
Example 1:
Peak usage: 2 Showers & Washing Machine = 6 gpm
Example 2:
Peak usage: 4 Showers & Dish Washer = 10 gpm

## Slide 5
STEP THREE
Select the proper unit or pair of units using the sizing chart found online or in the product catalog.
Simply find the Temperature Rise on the left then match up a unit or pair of units that provides the approximate flow rate needed.
Example 1:
Peak usage: 2 Showers & Washing Machine = 6 gpm
Example 2:
Peak usage: 4 Showers & Dish Washer = 10 gpm
Temp Rise: 65
Ideal Models:
EZ111, NRCR111, NRC111
Ideal Models:
Pair of EZ98, NRC98, NRCR92, NR98
Example 1
Example 2

## Slide 6: FINAL TIP:
It’s always better to slightly oversize than to undersize.
There’s virtually no downside to an oversized system for the home however and undersized system will not provide enough hot water for the home during all times of the year.