## Slide 1
EZ Start Plus App Screens

## Slide 2: OUTLINE
EZ Start Plus App
  Programming the Unit
  Built In Display
  Initial Set Up of the App
  Field Gas Conversions
  Unit Settings
  Saved Settings
  User Settings
  Recirc Timer Settings
  Error Code History
  Maintenance Monitors
  Trial Operation

## Slide 3: EZ START PLUS APP
Initial unit setup, temperature adjustment and maintenance can all be handled through the new EZ Start Plus Bluetooth App!
The App will walk you through setting up the unit upon completing installation and provides an easy way to register the unit for your customers.
Error Code History can be accessed and will link you directly to help articles related to any error codes stored.

## Slide 4: PROGRAMMING THE UNIT
Pro Series units no longer have physical dipswitches on the circuit board. All programming of the unit is done with the new EZ Start Plus App or the built-in display window.
Directions can be found in the manual

## Slide 5: BUILT IN DISPLAY WINDOW
Displays temperature setting, service reminders and error codes. Also allows you to view maintenance monitors, error code history and change installation settings. The new display window makes the remote control a truly optional item.

## Slide 6: INITIAL SETUP
Open EZ Start Plus App and select Contractor
Enter Passcode and tap “NEXT”
Make sure Bluetooth is ON
Select Unit then tap OK
Register Warranty or skip
If you select Other (e.g. Owner) the Unit Settings and Trial Operation Functions are disabled

## Slide 7: FIELD GAS CONVERSION
All Pro Series models are ready to be used with NG. If the jobsite has LP, a simple field gas conversion can be performed without the need to purchase any additional parts. Conversion is EZ and can be done in about 5 minutes.
Conversion Kit taped to top of unit
Contents of LP Conversion Kit

## Slide 8: FIELD GAS CONVERSION
Step 1
Remove screw
Step 2
Remove the c-clip
Step 3
Carefully remove gas fitting
Step 4
Remove 2 screws securing venturi fitting

## Slide 9: FIELD GAS CONVERSION
Step 5
Remove NG orifice
Step 6
Step 7
Insert gas fitting, secure c-clip and screw
Step 8
Secure venturi fitting
Insert LP orifice
(make sure o-ring and gasket aren’t lost or damaged)
O-RING
GASKET

## Slide 10: FIELD GAS CONVERSION
Step 10 (continued): Changing gas type to LP with EZ Start Plus App
Tap “Unit Setting”
Tap Change Setting, Tap LP then tap “DONE”
Tap “Convert Gas Type”
After a few seconds it should show complete
Step 9
Plug in LP conversion connector
*Built in display can also be used to convert gas type, see gas conversion directions included with unit

## Slide 11: FIELD GAS CONVERSION
MAKE SURE TO FILL OUT AND ATTATCH GAS CONVERSION STICKER TO UNIT

## Slide 12: UNIT SETTINGS
Tap “?” To get additional information on setting
Tap “Unit Setting”
Select Options Based on Installation then tap NEXT
Tap “2. Unit Setting”
Tap OK to Close

## Slide 13: UNIT SETTINGS
Upon completion, email app will open to allow emailing the installation settings to Noritz. This is not required, but very helpful for Customer Care.
Please fill out these items if you opt in to send
Review your selections then tap DONE
App programs unit
Tap OK when complete
If you check the Copy Settings Temporarily, you can use the Apply Saved Settings for 6 hours.

## Slide 14: SAVED SETTINGS
Tap “Saved Setting 1”
Tap “Save the current settings”
The App will save model name and date in title
To rename title Tap “Change the title”
Type in name you want to reference the settings

## Slide 15: USER SETTINGS
Residential units are limited to 120 by default but they can be bypassed following these steps.
Power OFF then tap User Settings
Adjust Max Temp then tap Done
Tap Home icon to go back to home page
Adjust Temp then tap Set
Tap the power button to turn back ON
Adjusting the maximum output temperature settings
User Setting have a Drain Water and Scale Flushing Feature

## Slide 16: RECIRC TIMER SETTINGS
*Only NRCR will list Auto Timer
On Home page Tap “Recirculation Mode”
Select Type of Recirculation Mode*
The “View” button shows the schedule
Each day can be different, or you can copy from another day Tap “Copy”
Highlight the times you want recirculation running in RED
Tap “DONE” to save

## Slide 17: ERROR CODE HISTORY
Shows the number of days elapsed since the error was reported.
Tap the email icon to launch the email app to send data to Noritz Customer Care.
Tap the phone # to launch the phone app and call Noritz.
📨
To
Customer Care
Error history can be displayed, and content can be emailed to Noritz Customer Care.
Tap on the error code to link to the Noritz web site. Detailed error code info displayed.
Tap Maintenance Button
Tap Error History Button

## Slide 18: MAINTENANCE MONITORS
You can check and record up to 2 minutes of Maintenance Monitor data
and send to Noritz Customer Care.
Tap Maintenance Button
Tap MM# Info Button
Tap REC Button
Tap STOP Button or 2 minutes passed
Auto launches email after recording ended

## Slide 19: TRIAL OPERATION
Depending on the unit you can do a trial operation on:
Fan Motor, Igniter, Water Servo, Pump (NRCR only), or Bypass Servo (CDV only)
Tap Maintenance Button
Tap Trial Operation Button
Tap Toggle Button to turn ON
Tap Toggle Button to turn OFF
Select Part for Trial Operation

## Slide 20: HELPFUL LINKS
SUPPORT.NORITZ.COM
NORITZ.COM/TECHTIPS
HELP.NORITZ.COM
TRAINING.NORITZ.COM
YOUTUBE.COM/NORITZAMERICA
Customer Care: 866-766-7489

## Slide 21: THANK YOU