## Slide 1: CMK and CRK Commercial Systems
Introducing the new Noritz Complete Commercial System Bundles

## Slide 2
CMK and CRK Training Overview
Features and Benefits
CMK – CRK System Configurations
Designing Your CMK or CRK System
CMK Wall Mount Installation Overview
CRK-BASE + CMK-BB4 Shown, NCC199CDV Pro Units Sold Separately.

## Slide 3
Easy to Transport
Sturdy Aluminum Frame
Assembly uses only 12 Bolts vs 60 Bolts of Competitor Racks!
Install in Less Than 2 Hours
True Commercial Manifold
Best Value in the Industry
Retrofit Easy Button
CMK and CRK Systems Features & Benefits
CRK-BASE + CMK-BB4 Shown, NCC199CDV Pro Units Sold Separately.

## Slide 4
CRK-BASE Shown expanded to allow up to 4 units in a back to back configuration.
Assembly uses only 12 Bolts vs 60 Bolts of Competitor Racks!
Single CRK-BASE allows for 1-4 units, competitor requires Base + Extension to install more than 2 units.
Lighter weight corrosion resistant Aluminum frame vs. Heavier Coated Steel frame of competitor.
CRK-BASE Shown expanded to allow up to 4 units in a back to back configuration.
CRK-BASE Features & Benefits

## Slide 5
CMK-SS2
Wall Hanging Side by Side Commercial Manifold Kit featuring 2 NCC199CDV Tankless Water Heaters (sold separately)
Max BTU/h: 399,800
CMK-SS3
Wall Hanging Side by Side Commercial Manifold Kit featuring 3 NCC199CDV Tankless Water Heaters (sold separately)
Max BTU/h: 599,700
Side by Side
CMK-SS4
Wall Hanging Side by Side Commercial Manifold Kit featuring 4 NCC199CDV Tankless Water Heaters (sold separately)
Max BTU/h: 799,600
CMK (Commercial Manifold Kit) System Configurations

## Slide 6
CMK-BB2
Commercial Manifold Kit connecting 2 Back to Back NCC199CDV Tankless Water Heaters (sold separately) installed on CRK Base – Floor standing rack (sold separately)
Max BTU/h: 399,800
CMK-BB4
Commercial Manifold Kit connecting 4 Back to Back NCC199CDV Tankless Water Heaters (sold separately) installed on CRK Base – Floor standing rack (sold separately)
Max BTU/h: 799,600
CMK (Commercial Manifold Kit) System Configurations
Back to Back

## Slide 7
CRK-BASE
The CRK-BASE commercial rack kit allows for custom floor standing installations of 1 to 4 tankless units.
CRK-ADDON
The CRK-ADDON commercial kit lets you expand your existing system to more than 4 units.
CRK (Commercial Rack Kit) System Configurations

## Slide 8
CMK (Commercial Manifold Kit) Design Your System
Step 1
Designed for Use With Our NCC199CDV Pro Tankless
Select Desired Number of NCC199CDV Pro Tankless Needed for System

## Slide 9
CMK (Commercial Manifold Kit) Design Your System
Step 2
Choose Between Wall Hanging or Floor Standing System
CMK-SS
Wall Hanging Bundle Kits
CMK-SS2
CMK-SS3
CMK-SS4
CMK-BB
Floor Standing Bundle Kits
CMK-BB2
CMK-BB4

## Slide 10
CMK (Commercial Manifold Kit) Design Your System
Step 3
Select Your
CMK or CRK Configuration
Wall
Hanging Configurations
CMK-SS2
CMK-SS3
CMK-SS4
Floor
Standing Configurations
CMK-BB2
CMK-BB4

## Slide 11
CMK (Commercial Manifold Kit) Design Your System
Step 4
Choose the Floor-Standing Base
(For CRK Only)
The CRK-BASE commercial rack kit allows for custom floor standing installations of 1 to 4 tankless units.
Step 5
Select Optional Extension
(For CRK Only)
The CRK-ADDON commercial kit lets you expand your existing system to more than 4 units.

## Slide 12
CMK (Commercial Manifold Kit) Additional Notes
Common Header Diameter Recommendation
One CRK-ADDON may be used per CRK-BASE. Attempting to use multiple CRK-ADDON may result in misaligned water and gas manifolds.
Up to 24 NCC199CDV Pro heaters can be connected using multiples of the CRK-BASE and CRK-ADDON kits. Quick Connect Pro up to 6 units or use a 6, 12 or 24 unit system controller (sold separately) to ensure system balancing and load management.
NCC199CDV Pro units may be common vented, refer to the common vent manual for full details.
Manifold sizing is designed for a maximum of eight (8) water heaters. In order to connect units in greater number than eight, a common header of a larger diameter may be necessary. Refer to local plumbing and/or building code for minimum pipe sizing requirements.

## Slide 13
Cardboard Mounting Template
2” Hot Water Manifold
2” Cold Water Manifold
2” Gas Manifold
¾” Condensate Drain Manifold
2x Manifold Wall Mount Brackets
Clamps, Caps, Etc
See Page 3 of Installation Manual for full details
CMK (Wall Mount) In The Box
CMK (3 Unit Wall Mount) Installation Overview
In The Box

## Slide 14
Determine number of units to be mounted
Template may be folded if less than 4
Align left bracket mount with stud
Level template
Secure template to wall
Drill pilot holes
Remove template
CMK (Wall Mount) Mounting Template
CMK (3 Unit Wall Mount) Installation Overview
Using Mounting Template

## Slide 15
Attach iso kit unions to cold/hot fittings
Attach braided hose to condensate fitting
Attach gas union to unit
Attach condensate fitting to unit
CMK (Wall Mount) Preparing Heaters
CMK (3 Unit Wall Mount) Installation Overview
Preparing Heaters

## Slide 16
Mount heater brackets
Mount manifold wall brackets
Hang units
Make sure units are centered on bracket
Secure units to top bracket
CMK (Wall Mount) Mounting Brackets
CMK (3 Unit Wall Mount) Installation Overview
Mounting Brackets

## Slide 17
Units and brackets mounted
Mount hot water manifold
Mount condensate drain manifold
Mount gas manifold
Mount hot water manifold
Secure bottom bracket of units
CMK (Wall Mount) Manifold Installation
CMK (3 Unit Wall Mount) Installation Overview
Manifold Installation

## Slide 18
Assemble CRK-BASE
Prepare and Hang Units
Install Hot Water Manifold
Install Condensate Manifold
Install Gas Manifold
Install Cold Water Manifold
CRK (Floor Standing Rack) Installation Basics
CRK (4 Unit Back to Back) Installation Overview

## Slide 19
THANK YOU