## Slide 1
NRCB OVERVIEW
Introduction to the NRCB

## Slide 2
INTRODUCTION
Specifications
Key Features
Installation
Venting
Water Connections
Dip Switch Settings
Control Panel
Heating Control Settings
Electrical Wiring
Additional Accessories
Water Treatment
Maintenance Monitors

## Slide 3
SPECIFICATIONS
Models | NRCB180DV / NRCB199DV
Standard Gas Input | Min: 18k Max: 180k / Min: 18k Max: 199k
Heating Gas Input | Min: 18k Max: 100k / Min: 18k Max: 120k
DHW Flow Range | 0.4 – 9.8 GPM / 0.4 – 11.1 GPM
AFUE | 95%
DHW Burner Off Flow | 0.29 GPM
Heating Temp Range | 100F – 180F (As low as 80F with setting)
DHW Temp Range | 90F – 140F
Simultaneous Heating & DHW | YES
Max Elevation | 10,000 feet
Connection Sizes | ¾” DHW & Gas, 1” Heating, ½” Auto Feeder & Condensate
Quick Connect Capable | YES (With same BTU EZ or CDV Unit)
Outdoor Temp Sensor | INCLUDED
Warranty | 10 Year HEX, 5 Year Parts, 1 Year Labor

## Slide 4
KEY FEATURES
Simultaneous Operation of DHW & Heating
Quick Temperature Control and Stability
High DHW Flow Rates

## Slide 5
SIMULTANEOUS OPERATION
Heating Position
DHW Position
Hot Water
Heating
DHW
Hot Water
Most Competitor’s 3-Way Valve:
Either Heating or DHW.

## Slide 6
DHW
Heating
Heating
BOTH Heating and DHW!
SIMULTANEOUS OPERATION
NRCB 3-Way Valve:
Hot Water
Heating
DHW
Heating Position
DHW Position
Hot Water
DHW
Simultaneous Position
Hot Water
Heating
DHW

## Slide 7
QUICK TEMP CONTROL & STABILITY
Chart: Hot Water Speed: 2 GPM Flow
ONLY 1°F Overshoot
Overshoots OVER 10°F
 | Hot Water Speed |  | Overshooting Temperature
 | 110°F | 120°F | 
NRCB | 19 sec | 23 sec | 1°F
Competitor | 32 sec | 35 sec | 10°F

## Slide 8
QUICK TEMP CONTROL & STABILITY
Chart: 2GPM DHW while Heating at 180F
NO Temp Spike
Overshoots OVER 30°F
OVER 140°F for MORE than 30 sec.
 | Overshooting
 | Temp
NRCB | 0°F
Competitor | Over 30°F
Competitor REQUIRES an additional external thermostatic mixing valve for improved temperature stability
NO RISK of ever reaching dangerous scalding temperatures while heating

## Slide 9
HIGH DHW FLOW RATES
 | NRCB | Competitor
Water Pathway |  | 
Flow Control | Variable | Fixed
Max GPM (199k btu Model) | 11.1 GPM | 5.6 GPM
Min Activation | 0.4 GPM | 0.5 GPM
Min Operation | 0.29 GPM | Not Mentioned
COLD
COLD
HOT
HOT
Flow Restriction
(Fixed)
Flow Control
(Variable)
Bypass Control
Valve

## Slide 10
INSTALLATION

## Slide 11
VENTING & TOP OF UNIT
DV and SV Venting
OD Capable w/ VCK-NRCB
2” or 3” PVC/CPVC or PP
60ft w/ 2”
100ft w/ 3”
Heating Pressure Relief Valve
Exhaust
Intake

## Slide 12
BOTTOM CONNECTIONS
Heating Water Outlet (Supply)
Heating Water Inlet (Return)
Auto Feeder Water Inlet
Hot Water Outlet
(DHW)
Gas Inlet
Cold Water Inlet
(DHW)
Condensate Drain

## Slide 13
PRESSURE RELIEF VALVES
Domestic Side ¾” 150 psi
(Purchased Separately)
Heating Side ¾” 30 psi
(Included)

## Slide 14
*Default Setting
DIPSWITCH SETTINGS
OFF
ON
Set up the unit for expanding simultaneous, vent type, elevation, vent length and size.

## Slide 15
DIPSWITCH SETTINGS W/ PROCARD
Made simple using the PROCard APP!

## Slide 16
CONTROL PANEL

## Slide 17
DISPLAY SCREEN
If set to °F, Display will read Fahrenheit and Gallons per minute
If set to °C, Display will read Celsius and Liters per minute
Unit Display Type
Burner ON Icon
Freeze Prevention Icon
DHW Preheat Icon
DHW High Temperature Icon
DHW Icon
Heating Icon
Outdoor Reset Icon
Clock / Error Code / Temperature Display

## Slide 18
HEATING CONTROL SETTINGS
Standard (Manual Heating Settings) most common
Outdoor Reset Control
External Control (0-10 V) not common
There are 3 main ways to control the NRCB
When using Outdoor Reset there are 6 preprogrammed heating types and 1 custom type

## Slide 19
ELECTRICAL WIRING

## Slide 20
THERMOSTAT & AIR HANDLER WIRING
 | Rc-Y (Cooling) | Rc-G (Fan) | R-W (Heating)
Cool | Close | Close | Open
Heat | Open | Close | Close

## Slide 21
OUTDOOR RESET SENSOR WIRING
Outdoor Reset Sensor is included in the box with the Combi.
No additional charge!!!
It should be hardwired to the Combi’s Circuit Board Terminal CN 236 (O/S) to control the heating set temperature per the outside temperature. Energy Savings!!!
Installing the Outdoor Reset provides more options for different heating applications
Additional programming is needed to set up see installation manual
Avoid Areas with direct sunlight or near a heat source which may not be representative of true outdoor temperature
Outdoor Reset Sensor
Best location is on a N or NE facing wall, beneath the eaves, where the sensor is shielded from direct sunlight and moisture

## Slide 22
OPTIONAL EXTERNAL LWCO
Install LWCO above unit’s case
Disconnect Factory Installed Jumper Wire from CN 234 on Circuit Board
Wire LWCO Line to CN 234
Wire 24 VAC (max 0.5 Amps) to CN 231
LWCO needs to be above unit’s case
Factory Installed Jumper
24 VAC
LWCO Line

## Slide 23
OPTIONAL EXTERNAL PUMP WIRING
The Combi can control an External Pump
Pump must be 120V AC and 2 Amp Max
The pump should be used for the Secondary Loop in a Primary/Secondary Loop Application (Internal Pump in the Combi is the Primary Pump)
Additional programming is needed to set up an External Pump (see installation manual)
120 VAC for Pump Controls

## Slide 24
NEED MORE DHW?
Use the remote on the boiler
Slow closing solenoid valve is required between the NRCB and Tankless
The units will not rotate, and a recirculation system can be used.
Add a PRO Series Unit with a QC-2 Quick Connect Cord

## Slide 25
SOLENOID WIRING FOR QC SYSTEMS
Solenoid Valve must be
¾” 120V AC - 1.5 Amp Max
Solenoid Valve is needed when using a QC System with any PRO Unit
The Solenoid Valve must be Normal Closed Valve and Slow Closing to avoid water hammer

## Slide 26
ADDITIONAL ACCESSORIES
½” Pressure Reducing Valve Needed on the auto feeder connection line to reduce the inlet water pressure to below 30 psi
Air Separator
Required at the highest point of the heating system
Manifold Kit MK-NRCB-1
Premade to align with the heating supply and return ports. Shut off valves and ports to flush the HEX along with a drain port to bleed out air in the system

## Slide 27
WATER TREATMENT
Water Quality Guidelines in the Installation Manual should always be followed.

## Slide 28
MAINTENANCE MONITORS
General Combustion Information for Warranty Purposes
Data No. | Item Name | Multiplier | Units
01 | Total Heating Combustion Time | X 10 | Hours
02 |  | X 10,000 | Hours
03 | Total Plug In Time | X 100 | Hours
04 | Total DHW Combustion Time | X 1 | Hours
05 |  | X 1,000 | Hours
06 | Total Simultaneous Use of DHW & Heating | X 1 | Hours
07 | Number of DHW Ignition Times | X 100 | Time
08 |  | X 100,000 | Time
11 | Number of Heating Ignition Times | X 100 | Time
12 |  | X 100,000 | Time
78 | Total Circulation Pump Run Time | X 10 | Hours
79 |  | X 10,000 | Hours
Full list of Maintenance Monitors are located on the Technical Data Sheet inside the front cover of unit

## Slide 29
MAINTENANCE MONITORS
Flow, Temperature, Pressure and Error Code Information
Data No. | Item Name | Multiplier | Units*
14 | Total DHW Flow Rate | X 0.1 | gal/min
30 | DHW Inlet Temperature | X 1 | °F
31 | DHW Outlet Temperature | X 1 | °F
32 | DHW Heat Exchanger Temperature | X 1 | °F
34 | Heating Return Temperature | X 1 | °F
35 | Heating Supply Temperature | X 1 | °F
36 | Exhaust Temperature | X 1 | °F
38 | Outdoor Temperature Sensor Temp | X 1 | °F
67 | Heating Water Pressure | X 0.1 | psi
91-98 | Error Code History (91 is most recent) If 3 digit error code the first 2 digits will show and then flip to subdivision number, this will flip every 2 seconds |  | 
* If [I:00_FC] is set to C (Celsius) then units will be in lit/min and °C

## Slide 30
THANK YOU