## Slide 1
MAINTENANCE &
TROUBLESHOOTING
Level 2 Troubleshooting and Service,
Focused on the EZ, NRCR and CDV.

## Slide 2: OUTLINE
We will cover the following topics:
Recommended Tools
Water Quality & Descale Procedure
General Service & Maintenance
Common Error codes and Maintenance Monitors
½” Gas Line Requirements
Component Identification
PROCard App

## Slide 3: RECOMMENDED TOOLS
What’s in your tool bag?

## Slide 4: RECOMMENDED TOOLS
Phillips Screwdriver
Descale Kit
Digital Gas Manometer
Digital Multimeter
Air Compressor
Noritz Remote Control
While you can fully disassemble and reassemble a Noritz unit with only a long phillips screwdriver, you may not be able to complete all service or troubleshooting with only a screwdriver. A T15 Torx bit, flashlight and plumbers grease are also helpful to round out your tool kit.

## Slide 5: WATER QUALITY AND DESCALE PROCEDURE
Ensure a long life by addressing water quality issues per our guidelines.

## Slide 6: WATER QUALITY GUIDELINES
Water Quality Guidelines in the Installation Manual should always be followed. Softening or treating the water with a Scale Shield is best as it prevents scale build up from happening in the first place. Descales are good, but a last resort as you are cleaning up scale build up that could have been prevented.
Notes: Before we get into descaling we need to talk about water quality and why it’s important

## Slide 7: WATER QUALITY GUIDELINES
Here are some issues related to Hard Water or Poor Water Quality:
Scale Buildup
Heat Exchanger Leak
Overheated Water Temperature
Clogged Inlet Filter Screen

## Slide 8: WATER QUALITY GUIDELINES
All* units since 2016 have a “Flush Mode” used when descaling the unit.
*NC380-SV Does not have a flush connector.
PRO Series Models
2016+ Models
Directions can be found in the manual

## Slide 9: DESCALE EQUIPMENT
So, what do you need to perform a proper descale?
2 Flexible Hoses
5 Gallon Bucket
1/6 hp Submersible
Pump
50/50 Mix of Water and a Calcium, Lime and Rust Remover
Noritz Descale Kit Shown, Part # DSCL-KIT

## Slide 10
http://support.noritz.com
PROCard App
DESCALE DIRECTIONS
Youtube.com/Noritzamerica

## Slide 11: GENERAL SERVICE AND MAINTENANCE
Periodic maintenance items to keep the unit running at peak performance

## Slide 12
A descale takes 1 hour, that’s the perfect time to look over the unit and clean any areas that are dirty. This could include:
Checking intake and exhaust terminations
Checking internal intake filter
Cleaning ignition and flame rods
Cleaning fan motor and burner
MAINTENANCE ITEMS

## Slide 13
Remove 2 screws securing rods
CLEANING IGNITION & FLAME RODS
Clean with rough side of a sponge, Scotch-Brite pad, fine grit sandpaper (300+ grit)

## Slide 14
SHUT OFF GAS then remove mounting bracket (2 screws)
CLEANING FAN & BURNER

## Slide 15
Remove c-clip and carefully disconnect gas valve from venturi. There is an o-ring, be careful not to damage it.
CLEANING FAN & BURNER

## Slide 16
Disconnect fan wire harness then remove 4 screws securing it to burner.
CLEANING FAN & BURNER

## Slide 17
Remove fan motor and venturi from unit and remove venturi from fan.
CLEANING FAN & BURNER

## Slide 18
Clean the fan with an air compressor, vacuum, plastic brush or any combination of those items. If the fan cannot be cleaned effectively, the fan should be replaced. DO NOT SPLIT THE FAN HOUSING.
CLEANING FAN & BURNER

## Slide 19
When reassembling, line up the gas connection with the triangle stamped on the fan housing. Be careful not to damage or lose any o-rings or gaskets on the fan housing.
CLEANING FAN & BURNER

## Slide 20
Use a vacuum to clean the burner. DO NOT USE AN AIR COMPRESSOR ON THE BURNER! The burner mesh could be damaged and cause additional problems.
CLEANING FAN & BURNER

## Slide 21: COMMON ERROR CODES

## Slide 22
COMMON ERROR CODES
Error Code | Description
11 | Ignition Failure (Failure to detect flame)
12 | Flame Loss
16 | Abnormally High Outlet Temperature
20 | High Limit Switch
63 | Recirculation Abnormality
65 | Main Water Control Servo Abnormality
66 | Bypass Water Control Servo Abnormality
73 | Circuit Board Setting Abnormality
F76 | Multi System Communication Error
90 | Combustion Abnormality

## Slide 23: TECHNICAL DATA SHEET
This sheet is inside a zip bag taped to the inside of the front cover and gives you the most commonly requested technical data.

## Slide 24
Shows the number of days elapsed since the error was reported.
Tap the email icon to launch the email app to send data to Noritz Customer Care.
Tap the phone # to launch the phone app and call Noritz.
📨
To
Customer Care
Error history can be displayed, and content can be emailed to Noritz Customer Care.
Tap on the error code to link to the Noritz web site. Detailed error code info displayed.
Tap Maintenance Button
Tap Error History Button
EZ START PLUS ERROR HISTORY

## Slide 25
11 Error Code: Ignition Failure (Failure to Detect Flame)
Air
Fuel
Spark
11 ERROR CODE
Model: | NG | LP
EZ, NRCR, NCC199CDV | 3.5” to 10.5” WC | 8” to 14” WC
This code indicates a lack of spark or lack of gas entering the burner. Three things needed for combustion are:
However, you can cross off Air as a cause by simply removing the front cover. Start simple with troubleshooting, don’t jump to the most complicated possibility. Simple steps like verifying inlet gas pressures are within range and cleaning the ignition rods.

## Slide 26
12 Error Code: Repeated Flame Loss
12 ERROR CODE
This code indicates the unit cannot maintain flame in the burner. Just like the error code 11, insufficient inlet gas pressures can also cause the flame to go out.
Incorrect Venting
Verify Inlet Pressure
Check/Clean Flame Rod
Check Grounds
Model: | NG | LP
EZ, NRCR, NCC199CDV | 3.5” to 10.5” WC | 8” to 14” WC

## Slide 27
16 & 20 ERROR CODES
16 Error Code: Abnormally High Output Temp
20 Error Code: High Limit Switch
Scale deposits in the heat exchanger and/or water components
Wrong gas type
Scale deposits in the heat exchanger
Poor Combustion
Bad Wiring or Failed High Limit Switch

## Slide 28
63 Error Code: Recirculation Abnormality (NRCR Only)
63 ERROR CODE
This code indicates the unit is trying to run the recirculation pump but is not detecting any flow.
  Check Return Line Filter and Water Shut Offs
  Purge air in the domestic hot and return line (Dedicated Mode)
  Check that the “Crossover” connector is connected together
  Check crossover valve filter (Crossover Mode)
New Installations:
Older Installations:
  Check Return Line Filter and Water Shut Offs
  Circuit Board
  Recirc Pump
  Recirc Flow Sensor

## Slide 29
65 Error Code: Main Servo Abnormality
66 Error Code: Bypass Servo Abnormality
65 & 66 ERROR CODES
Both error codes indicate a problem communicating with or positioning the respective water servo.
Main Servo
Bypass Servo

## Slide 30
73 & F76 ERROR CODES
If dipswitches were changed or other connectors changed while unit has power a 73 code will appear. Unplug unit, finalize all dipswitch and wiring changes, and plug in heater.
Also occurs if the circuit board was replaced but not programmed.
Make sure only 1 remote control is hooked up when there are 2 units quick connected.
73 Error Code: Circuit Board Setting Abnormality
F76 Error Code: Multi System Communication Error

## Slide 31
90 Error Code: Combustion Abnormality
90 ERROR CODE
This code indicates the unit is not able to hit the set temperaure.
Most commonly caused by restrictions in the venting (intake and/or exhaust), incorrect dipswitch settings, a clogged or restricted condensate drain line or insufficient gas pressure going to the unit.
Older installs may have a dirty fan or venturi reducing the amount of air and gas that makes it into the burner.

## Slide 32
90 Error Code: Combustion Abnormality
90 ERROR CODE
Use the PROCard App to verify correct dipswitch settings.

## Slide 33
90 Error Code: Combustion Abnormality
90 ERROR CODE
Use the EZ Start Plus App or Operation Panel to verify correct settings.

## Slide 34
LESS THAN IDEAL INSTALLS

## Slide 35: COMMON MAINTENANCE MONITORS

## Slide 36
Commonly used maintenance monitors for troubleshooting and service
MAINTENANCE MONITORS
Residential Remote
Commercial Remote
MM14: Flow Rate
MM30: Inlet Water Temp
MM31: Outlet Water Temp
MM32: Heat Exchanger (HEX) Water Temp
MM86: Recirculation Mode (NRCR)

## Slide 37
You can check and record up to 2 minutes of Maintenance Monitor data
and send to Noritz Customer Care.
Tap Maintenance Button
Tap MM# Info Button
Tap REC Button
Tap STOP Button or 2 minutes passed
Auto launches email after recording ended
EZ START PLUS MAINT MONITORS

## Slide 38
MM14 FLOW RATE
Tankless heaters activate and remain on based on a minimum flow rate (usually .5 gallons per minute [gpm]).
Units are on demand and they modulate in real time based on the following conditions: Flow Rate, Set Temp and Incoming Water Temp.
The tankless doesn't do anything when a faucet is opened.
The tankless shuts off after the water temp is adjusted.
The recirculation pump doesn't activate the unit.
Those are just a few examples of common complaints that you can start troubleshooting with MM14

## Slide 39
MM30 INLET WATER TEMP
While this MM might not be as widely used as the others, it can still provide additional insight into why the heater is or is not doing something.
If the complaints are related to heater performance, such as not enough flow in the winter time or the heater doesn’t activate in the summer time, you can use MM30 to establish the temperature rise and the BTU demand.
BTU Formula:
BTU = Flow Rate in GPM x Delta T x 500
Lets say the customers faucet flows .6 gpm, their set temp is 115 and the inlet water temp is 87. The Delta T is 28 (115 minus 87). Now let's put all those numbers into the formula:
8,400 BTU
.6
x 28
x 500 =

## Slide 40
MM31 OUTLET WATER TEMP
Along with MM14 (Flow Rate) this MM is one of the most used. This will tell you the temperature of the water leaving the unit. If you get any questions or complaints regarding hot water temperature this MM will be very useful.
The water at the fixture doesn't feel hot enough.
The water temperature seems to fluctuate greatly.
The bathroom sink gets hot but the shower doesn’t.
The unit has a 90 error code.
The units goal is to get up to set temp as quickly as possible and maintain that temp as long as there is enough flow. Once the water leaves the unit, there are many things that can result in the water temp at the fixture being different. If the water temp leaving the unit is at set temp, the problem likely is with the plumbing or the fixtures.

## Slide 41
MM32 HEAT EXCHANGER WATER TEMP
This MM is very helpful to determine if the burner is heating up the water in the HEX properly. It is also useful in troubleshooting a 90 error code (along with MM31).
Let's say you have a call for EC90 and you have determined it's because the unit is not hitting set temp. Why is the outlet temp low? Let's find out.
If MM32 shows 140, but MM31 shows 100 it would indicate there is a problem with the bypass servo (failed, stuck or debris in it).
If MM32 is also low, say 105 or 110 and MM31 shows 100 it would indicate the burner is not heating up the HEX high enough. Most likely not enough gas is entering the burner.
Both above examples would lead you down two very different troubleshooting paths so that's why checking MM32 is important when diagnosing low outlet temps.

## Slide 42
MM86 RECIRCULATION MODE
This MM is specific to the NRCR Series. It will tell the recirculation mode the unit is set to. This is helpful to verify that the recirc mode is actually set the way you think it is.

## Slide 43
Under certain specific conditions, a ½” gas line can be used. The length is equivalent length and factors in fittings and elbows.
½” GAS LINE DETAILS

## Slide 44: COMPONENT IDENTIFICATION
Circuit Board
Gas System
Gas Valve
Venturi
Fan Motor
Ignition System
Igniter
Ignition Rod
Heat Exchanger Assembly

## Slide 45
PARTS LIST
Helpful to locate parts and what they connect to.

## Slide 46
TRIAL OPERATION
Tap Maintenance Button
Tap Trial Operation Button
Tap Toggle Button to turn ON
Tap Toggle Button to turn OFF
Select Part for Trial Operation
Depending on the unit you can do a trial operation on:
Fan Motor, Igniter, Water Servo, Pump (NRCR only), or Bypass Servo (CDV only)

## Slide 47: CIRCUIT BOARD
Control center of the unit.

## Slide 48: GAS VALVE
Pre-mix units have a negative pressure gas system. DC voltage opens the main gas solenoid and the negative pressure created by the fan draws gas out of the valve and into the venturi.

## Slide 49: VENTURI
This is specific to the Pre-Mix type units. Air and Gas are introduced here and then enter the Fan Housing to be mixed before entering the Burner

## Slide 50: FAN MOTOR
In Pre-Mix units, the fan acts as a blender and mixes the air and gas together before pushing it into the burner.

## Slide 51: IGNITION SYSTEM
Igniter and Ignition Rods. Responsible for creating spark to ignite the air/fuel mixture.

## Slide 52: HEAT EXCHANGER ASSEMBLY
Transfers heat from the burner and exhaust into the water.

## Slide 53
The PROCard App (available for both iOS and Android) is a great tool to have on your phone!
Warranty Registration
Service Registration
Troubleshooting
Manuals
PROCard App
PROCARD APP

## Slide 54
866-766-7489
Please have readily available:
Model Number
Serial Number
Being onsite with the unit is not mandatory, but very helpful!
Model Number
Serial Number
CONTACTING CUSTOMER CARE
(866) - 7NORITZ

## Slide 55
SUPPORT.NORITZ.COM
NORITZ.COM/TECHTIPS
HELP.NORITZ.COM
TRAINING.NORITZ.COM
YOUTUBE.COM/NORITZAMERICA
Customer Care: 866-766-7489
HELPFUL CONTACT INFO

## Slide 56
THANK YOU