## Slide 1
Change Log (Hidden Slide):
6/11/2026: Updated slide 23 Ext Recirc to Reference RPK-EXT-P without remote is available for Pro Series

## Slide 2: RESIDENTIAL LEVEL 1
Product Line, Accessories and Installation Basics

## Slide 3: READ THE MANUAL
Tankless units are combustion appliances that contain gas, water and electricity in a unit the size of a suitcase.
The proper, safe and reliable operation of our units is 100% contingent on a correct installation and proper maintenance throughout its life.

## Slide 4: TRAINING SECTIONS
Residential Product Line:
Standard Efficiency
High Efficiency
Pre-mix Units
EZTR Packages
Installation:
Unit Sizing
Gas Line
Choosing Location
Venting
Condensate Line
EZ Start Plus App
Circuit Board Dipswitches
Install Checklist
Maintenance:
Water Quality
Water Treatment
Cleaning Unit

## Slide 5: WHAT IS A TANKLESS WATER HEATER?
A tankless water heater uses a burner and heat exchanger to produce an endless supply of hot water on-demand.
About
400F
About
400F
Primary Heat Exchanger
About
400F
About
120F
Primary Heat Exchanger
Secondary Heat Exchanger
Condensate
Collector
Water is heated using the hot exhaust gas.
Fan
Fan
Cold In
Cold In
Gas In
Gas In
Hot Out
Hot Out
Tankless Operation:
Hot water fixture is opened
Tankless detects flow
Burner ignites
Water is heated in the Heat Exchanger
Hot water exits the tankless to the fixture
Fixture is closed and tankless shuts off
High Efficiency Unit
Standard Efficiency Unit

## Slide 6
NR98SV
Max 199k btu
Non-Condensing Units
120k to 199k btu
UEF = 0.82
Indoor and Outdoor Units Available (7 units total)
Indoor Units Require Cat III Stainless Steel Venting
All Units Satisfy 20ppm Low NOx Requirements
Copper Heat Exchanger
12 Years Heat Exchanger
5 Years All Other Parts
1 Year Reasonable Labor
STANDARD EFFICIENCY UNITS

## Slide 7
HIGH EFFICIENCY UNITS
NRC98DV
Max 180k btu
Condensing Units
120k to 199k btu
UEF = 0.87 to 0.92 (depending on the unit)
Indoor and Outdoor Units Available (8 units total)
Indoor Units Use 3” or 4” PVC/CPVC/PP
All Units Satisfy 20ppm Low NOx Requirements
Copper Primary Heat Exchanger
Stainless Steel Secondary Heat Exchanger
12 Years Heat Exchanger
5 Years All Other Parts
1 Year Reasonable Labor

## Slide 8
NRC98DV
Max 180k btu
All units include either an external remote control or built in display window for easy indication of set temperature along with monitoring and diagnostics capability.
NRC661DV
Max 120k btu
STANDARD & HIGH EFFICIENCY UNITS
NR66OD
Max 120k btu
NR98SV
Max 199k btu

## Slide 9
Pre-Mix refers to how the air and gas is pre-mixed in the fan before entering the burner
Pre-Mix units have Dual Stainless Steel Heat Exchangers
The Noritz Pre-mix Lineup:
EZ PRO Series
NRCR PRO Series
NRCB Boiler
NCC199CDV PRO (commercial unit)
HIGH EFFICIENCY PRE-MIX UNITS

## Slide 10: OVERVIEW
Available Models:
EZ71DV: 12,800 – 160,000 BTUh / 0.4 - 9.0 gpm
EZ98DV: 12,800 – 180,000 BTUh / 0.4 - 9.8 gpm
EZ111DV: 12,800 – 199,900 BTUh / 0.4 – 11.1 gpm
Key Features:
Top Mounted Water Connections
UEF = 0.98
EZ Start Plus Bluetooth® App
Built-in Operation Panel
Field Gas Conversion (included in the box)
Versatile Venting (one model for Indoor and Outdoor installations)
2”, 3” or 4” PVC/CPVC/PP
  2” Max length: 75’
  3” Max length: 150’
  4” Max length: 65’
Flexible 2” SV up to 35’
25 Year Heat Exchanger Warranty

## Slide 11: GAS CONVERSION
All PRO Series models are ready for use with NG and include a simple field gas conversion to LP.

## Slide 12: OVERVIEW
Available Models:
NRCR92DV: 12,800 – 165,000 BTUh / 0.4 - 9.2 gpm
NRCR111DV: 12,800 – 199,900 BTUh / 0.4 – 11.1 gpm
Key Features:
Built-In Recirculation Pump
UEF = 0.98
EZ Start Plus Bluetooth® App
Versatile Venting (Just like EZ Pro Series)
Steady BTU Control
15 Year Heat Exchanger Warranty
Recirc Setting:
Auto Learning (Default)
Manual Timer (Using EZ Start app or Operation Panel)
Title 24 (On Demand)
Recirc Types:
Dedicated Recirculation
Crossover (up to 2)

## Slide 13: VENTING
The NRCR PRO is a pre-mix style unit and thus has the same venting options as the EZ PRO Series:
DV Direct Vent
SV Single Vent
OD Outdoor
No Roof Kit
FSV Flexible Single Vent
Common Vent Capable (2 Units Quick Connected)

## Slide 14: DEDICATED
Return Line should have a shut off valve, hose bibb and expansion tank

## Slide 15: CROSSOVER
When using a crossover valve, the minimum set temperature is 120 F

## Slide 16: 2 CROSSOVER
Return Water
Hot Water
Cold Water
Hot Water
Return Water
Cold Water
Crossover Kit: CSV-BPK
Crossover Valve: cCS-V

## Slide 17: AUTO LEARNING
Auto Learning mode memorizes the customers usage patterns and automatically runs the pump during the hours hot water is needed. If the customers patterns change, the unit will adapt and remove times when it appears the customer no longer uses hot water.

## Slide 18
Schedule the NRCR PRO recirc times manually with the EZ Start Plus App. Simply tap the hours you want the pump to run.
Want the same schedule every weekday? Adjust the schedule for one day then copy to all weekdays.
No longer requires extra purchase!
MANUAL SCHEDULE

## Slide 19
On Demand mode only runs the pump when the customer presses a button or activates a motion sensor.
TITLE 24 ON DEMAND
Rocker Switch (IHK-RS)
Wireless Push Button Kit (WLB)
Optional Motion Sensor (WLB-MS)

## Slide 20
EZ Tank Replacement of a 40 Gallon Tank
Bundle kits include Unit, Isolation Valves and 25’ Flex Vent Kit (35’ Optional, sold separately)
Top Mounted Water Connections
120k Max btu High Efficiency Unit
6.6 gpm Max
UEF = 0.87
Copper Primary HEX and SS Secondary HEX
12 Year Heat Exchanger Warranty
The EZTR40 can only be used when replacing a tank and using the flexible venting, it cannot be adapted to vent with PVC or other rigid plastic venting.
EZTR40 PACKAGE

## Slide 21
EZ Tank Replacement of a 50 or 75 Gallon Tank
Bundle kits include Unit, Isolation Valves and 25’ Flex Vent Kit (35’ Optional, sold separately)
Top Mounted Water Connections
EZTR50 includes EZ98 PRO Unit (180k btu/9.8 gpm)
EZTR75 includes EZ111 PRO Unit (199k btu/11.1 gpm)
Dual Stainless Steel Heat Exchangers
UEF = 0.98
Built-in Operation Panel
EZ Start Plus Bluetooth® App
Field Gas Conversion
25 Year Heat Exchanger Warranty
EZTR50 & EZTR75 PACKAGES

## Slide 22
Use existing 3” or 4” round b-vent
(no oval vent or common venting with other appliance)
25’ included with EZTR package.
35’ vent kit optional, part # EZ2FVK-2
NOTE: Flexible vent can be shortened but you cannot join 2 pieces of flexible vent to extend the length.
Example: If you need 30’, you would buy the 35’ kit and cut off 5’. You would not attach an extra 5’ to the included 25’ kit.
EZTR PACKAGES

## Slide 23
Many Noritz units are compatible with external recirculation pumps such as the Noritz RPK-EXT pump kit.
Important Notes:
Display Window Units are not compatible with the RPK-EXT pump kit as they do not have a pump control connection. An externally controlled pump may still be used though
Single unit installations only (Will not work with Quick Connected Systems)
Remote included with RPK-EXT kit is optional on EZ Pro and CDV Pro units that use the EZ Start Plus App
RPK-EXT-P Kit available without remote control for EZ Pro or CDV Pro installations
RPK-EXT
Pump Kit
EXTERNAL RECIRCULATION

## Slide 24
Typical Recirc Diagram
Size pump for 2 gpm max flow
Control pump with timer or aquastat or use pump connection wires inside unit
Set aquastat 10 degrees below unit set temperature
EXTERNAL RECIRCULATION

## Slide 25
Proper sizing is a key aspect of the customers experience and satisfaction with their tankless.
An undersized tankless will provide the proper temperature but the customer will not be able to run as many hot water fixtures at the same time as they want.
This problem will be more apparent in the wintertime as the cold-water temperatures are even colder.
HOW TO SIZE A TANKLESS

## Slide 26
Step 1: Determine your maximum temperature rise. This is the difference between the tankless set temp and the wintertime ground water temp (aka Delta T)
For the purpose of this example let’s say the home is on the central coast of California.
Based on the map, we’ll say the winter ground water temp is 55 F.
Now you can determine the wintertime temperature rise:
120 Set Temp – 55 Ground Water Temp = 65 Delta T
HOW TO SIZE A TANKLESS: STEP 1

## Slide 27
Step 2: Determine the peak hot water demand of the home. If possible, ask the homeowner.
Shower: 2 gpm
Lav Sink: 1 gpm
Kitchen Sink: 1.5 gpm
Dishwasher: 2 gpm
Washing Machine: 2 gpm
Fixtures and appliances all have different flow rates depending on manufacturer however you can use an average amount to get a ballpark figure:
Example 1:
Peak usage: 2 Showers & Washing Machine = 6 gpm
Example 2:
Peak usage: 4 Showers & Dishwasher = 10 gpm
HOW TO SIZE A TANKLESS: STEP 2

## Slide 28
Step 3: Select the proper unit or pair of units using the sizing chart found online or in the product catalog.
Simply find the Temperature Rise on the left then match up a unit or pair of units that provides the approximate flow rate needed.
Example 1:
Peak usage: 2 Showers & Washing Machine = 6 gpm
Example 2:
Peak usage: 4 Showers & Dish Washer = 10 gpm
Temp Rise: 65
Ideal Models:
EZ111, NRCR111 or NRC111
Ideal Models:
Pair of EZ98, NRC98 or NRCR92
Example 1
Example 2
HOW TO SIZE A TANKLESS: STEP 3

## Slide 29
Final Sizing Tip:
It’s always better to slightly oversize a tankless system than to undersize it.
There’s virtually no downside to an oversized system for the home however and undersized system will not provide enough hot water for the home during all times of the year.
HOW TO SIZE A TANKLESS: FINAL TIP

## Slide 30
For large residential applications
2 compatible Noritz units may be
quick connected to double the
hot water output.
Part #: QC-2
QUICK CONNECT SYSTEMS

## Slide 31
The system will automatically
rotate primary and secondary
roles to ensure even use of
both units.
Primary
Secondary
QUICK CONNECT SYSTEMS
Part #: QC-2

## Slide 32
When there's a small demand, only the primary heater will fire up to meet the demand.
Primary
Secondary
QUICK CONNECT SYSTEMS
Part #: QC-2

## Slide 33
If the demand increases the primary unit will activate the secondary unit to help meet the demand.
QUICK CONNECT SYSTEMS
Primary
Secondary
Part #: QC-2

## Slide 34
Only the PRO Series and larger residential units with an external remote are compatible with the quick connect cable, smaller display window units are designed for single unit installations.
Quick Connect
Compatible
Not Quick Connect
Compatible
QUICK CONNECT SYSTEMS

## Slide 35
Of equal importance to a proper sized unit, is a properly sized and installed gas line to ensure adequate gas pressure.
Afterall, what good is selecting the perfect tankless if the gas system can’t support it’s needs?
GAS LINE SIZING
NATURAL GAS
3.5 TO 10.5 INCHES
PROPANE GAS
8.0 TO 14.0 INCHES
Required Gas Supply Pressure
* Supply pressures may vary unit to unit, refer to rating plate for exact pressure range

## Slide 36
GAS PRESSURE CHECK
Check the pressure when the unit is sitting idle (Static Pressure)
Check the pressure when the unit is in high fire (Dynamic Pressure)
Check the pressure on the gas connection or the bottom port of gas valve using T15 torx.
1) Locate and shut off gas valve
2) Zero manometer then connect to inlet port
3) Open gas valve and note static pressure
4) Create a high flow to ensure unit is in high fire and note dynamic pressure

## Slide 37
PRO Series installation manuals contains 5 sizing tables for hard pipe gas lines, 4 for NG and 1 for LP.
To pick what NG chart you use, you will need to know the initial supply pressure.
GAS LINE SIZING

## Slide 38
After determining the initial supply pressure, you can use the charts to determine the maximum equivalent length of ½” hard pipe you may use based on the max btu of the unit.
½” GAS LINE CONSIDERATIONS

## Slide 39
The higher the initial supply pressure, the longer the ½” gas line can be.
½” GAS LINE CONSIDERATIONS
Highlighted areas indicate max equivalent length for an EZ71DV (160k btu max). Equivalent length factors in elbows and fittings, not just straight pipe.

## Slide 40
Both Dedicated and Branching from an existing gas line are acceptable choices.
DEDICATED OR BRANCH GAS LINE?

## Slide 41
However, if you branch off the existing gas line, you need to make sure all sections of the line can support the btu demand.
Section 1
(300k btu)
Section 2
(240k btu)
Section 3
(200k btu)
DEDICATED OR BRANCH GAS LINE?
60k btu
40k btu
200k btu

## Slide 42
Also make sure the gas meter can supply the total btu demand of the home.
60k btu
40k btu
250 CFH
DEDICATED OR BRANCH GAS LINE?
Check Rating Plate on Meter
300k btu = total of all gas appliances
200k btu

## Slide 43
In some cases, it may need to be upsized to handle the added demand of the tankless unit.
DEDICATED OR BRANCH GAS LINE?
60k btu
40k btu
425 CFH
200k btu

## Slide 44
If using the PRO Series units only an Orifice Change and programing with EZ Start Plus App is needed. LP Orifice is included with the unit.
PROPANE TANK & ORIFICE
PROPANE GAS
8.0 TO 13.0 INCHES

## Slide 45
Now that you’ve sized out the perfect unit for the job and made sure the gas system can support the new tankless, it’s time to pick the perfect installation location.
CHOOSING INSTALLATION LOCATION

## Slide 46
For cold climates where snow is a regular or even occasional occurrence, you’ll want to install the unit indoors.
CHOOSING INSTALLATION LOCATION

## Slide 47
For warm climates that never see freezing weather, installing the unit outdoors is a great way to free up space inside the home.
CHOOSING INSTALLATION LOCATION

## Slide 48
Keep in mind all tankless water heaters have motorized parts. When in operation they are fairly quiet, but the noises may bother some customers so keep that in mind when scouting a location to install the unit.
CHOOSING INSTALLATION LOCATION

## Slide 49
If possible, avoid installing the unit on a bedroom wall or other areas where customers might expect a quiet space.
CHOOSING INSTALLATION LOCATION

## Slide 50
When installing the unit indoors, you have a few different venting options available to you although they will generally fall into 1 of 2 categories:
DV Direct Vent
SV Single Vent
INDOOR VENTING OPTIONS

## Slide 51
Two Pipes
To Outside
Concentric
Terminations
DVC Style
Unit
INDOOR VENTING OPTIONS
Direct Vent Examples:

## Slide 52
Single Vent Examples:
DV to SV
Conversion
Flex Vent
Kit
SV Style
Unit
INDOOR VENTING OPTIONS

## Slide 53
All Noritz indoor units may be vented either horizontally or vertically regardless of SV or DV vent type, with the only exception being the EZTR packages that use the 2” flexible vent.
HORIZONTAL OR VERTICAL VENTING

## Slide 54
Standard efficiency non-condensing units must be vented with category III stainless steel venting and high efficiency condensing models may use plastic venting such as PVC, CPVC or PP depending on code requirements.
VENTING MATERIAL
Non-Condensing
Model
Condensing
Model

## Slide 55: PVC VENTING
Horizontal Exhaust runs should pitch towards the unit to allow condensation to drain in the unit and out the trap.
Long Sweep Turns vs Short Radius Turns
Long sweep 90 creates a smooth transition of the exhaust gases from one direction to another
Long sweep 90 causes the least amount of turbulence.

## Slide 56: VENTING OPTIONS
One SKU, All Venting Options.
Direct Vent
Single Vent
Outdoor
No Roof Kit
Flex Vent Kit

## Slide 57
DV – Direct Vent
Ideal For:
Areas with dirty combustion air
Tight locations without combustion air
When unit is installed in a conditioned space (Why draw conditioned air through the unit?)
VENTING OPTIONS

## Slide 58
SV – Single Vent
Ideal For:
Areas with clean combustion air
Areas with plenty of combustion air
VENTING OPTIONS

## Slide 59
OD – Outdoor
Ideal For:
Warm climates without snow
Reclaiming space in the home
VENTING OPTIONS

## Slide 60
NRK – No Roof Kit
Ideal For:
Straight up b-vent runs 8.5’ or under
Tank Retrofits
Saving time by not replacing venting or getting on the roof
VENTING OPTIONS

## Slide 61
FSV – Flexible Single Vent
Ideal For:
B-vent runs with 45 degree turns
B-vent runs 5’ to 35’
Tank Retrofits
Saving time by not replacing venting
VENTING OPTIONS

## Slide 62
EZTR installations must be run vertically through the existing round b-vent and cannot be run horizontally.
EZTR FLEX VENTING

## Slide 63
When combustion air is likely to be contaminated, such as in:
Attics
Laundry Rooms
Commercial Kitchens
It’s best to install a Direct Vent unit.
WHEN TO DIRECT VENT

## Slide 64
Pulling in dirty combustion air with an SV unit will require quite a bit of preventative maintenance and likely shorten the overall lifespan of the unit.
WHEN TO DIRECT VENT

## Slide 65
2 PIPE TERMINATION OPTIONS
Direct Vent Vertical
Direct Vent Horizontal
Using PVT-HL terminations the distance between the intake and exhaust is 3 ft
Using 90 PVC elbows the distance between the intake and exhaust is 1 ft

## Slide 66
PVC-2CT: 2" Connections
PVC-3CT: 3" Connections
CONCENTRIC HORIZONTAL TERMINATION

## Slide 67
PVC-UCVK: For easy up and out venting
CONCENTRIC HORIZONTAL TERMINATION

## Slide 68
PVC-2LPT: 2" Connections
PVC-3LPT: 3" Connections
CONCENTRIC HORIZONTAL TERMINATION

## Slide 69
PVC-2CT: 2" Connections
PVC-3CT: 3" Connections
PRC-1: Plastic Rain Cap
CONCENTRIC VERTICAL TERMINATION

## Slide 70
If the installation location meets the combustion air requirements in the manual, you have the option to install a Single Vent unit or use the SV conversion kit on a compatible DV unit and run a single exhaust vent to the outside.
SV TERMINATION OPTIONS

## Slide 71
Outdoor installations are probably one of the easiest options if the climate allows. However, there are still things to consider such as clearances to building openings and how close the unit is to a neighboring building. The last thing you want is for the exhaust or operational noises to affect the neighbors.
OUTDOOR INSTALL CONSIDERATIONS

## Slide 72
The EZ PRO and NRCR PRO units can be common vented
COMMON VENTING 2 PRO SERIES UNITS
*The Btu/h input of the unit will be reduced by up to 9%.

## Slide 73
The terminations of all gas burning appliances are subject to National Fuel Gas Codes clearance requirements to building openings. The installation manual provides these diagrams and many clearance requirements directly from the national fuel gas code for both US and Canada.
INSTALLATION CLEARANCE REQUIREMENTS

## Slide 74
It’s important to note that Noritz does not make these clearance requirements and thus cannot overrule any local, state, provincial or national code. When there is no national code clearance listed, local code or the requirements of the gas supplier must be followed.
INSTALLATION CLEARANCE REQUIREMENTS

## Slide 75
These codes are designed to prevent the exhaust from a gas burning appliance from entering the home and putting the occupants at risk.
INSTALLATION CLEARANCE REQUIREMENTS

## Slide 76
Condensing heaters will have a ½” condensate drain connection on the bottom of the unit.
CONDENSATE DRAIN CONNECTION

## Slide 77
The condensate drain line should be as short and direct as possible and you do not need to create a trap as that’s what the collector inside the unit does.
CONDENSATE DRAIN CONNECTION
Adding an air vent on the condensate line will help with draining the condensate and not backing up into the unit.

## Slide 78
If the desired drain location is a long distance from or above the heater, a condensate pump should be used. The pump should be sized to handle 2 gallons per hour.
CONDENSATE DRAIN CONNECTION

## Slide 79
In cold climates with freezing weather, the condensate should not be drained to the outside as the condensate line could freeze and the heater will stop operating.
CONDENSATE DRAIN CONNECTION

## Slide 80
The drain line should be plastic as the acidic condensate will corrode metal pipes and the line should be no smaller than ½”.
Horizontal runs should be sloped downward a ¼” for every 1 foot of piping.
Make sure you leave an air gap at the end of the drain line.
CONDENSATE DRAIN CONNECTION

## Slide 81
The condensate collector inside the unit that should be pre-charged with water to prevent carbon monoxide leakage during initial operation of the unit. Pre-mix models such as the EZ series need about 10 oz of water while traditional condensing units like the NRC111 need about 30 oz.
FILLING CONDENSATE TRAP

## Slide 82
If you forget to pre-charge the condensate collector, make sure the installation area is well ventilated for the first 15-20 minutes of operation as the unit creates condensate and fills the collector.
FILLING CONDENSATE TRAP

## Slide 83
Treating the acidic condensate created by high efficiency units may be required by local code and is a good practice even if code doesn’t require it.
NEUTRALIZING THE CONDENSATE

## Slide 84
Noritz offers external neutralizers to raise the pH level of the acidic condensate to that of water so it can be drained safely.
The residential neutralizer is recommended to be installed 1 per unit.
NEUTRALIZING THE CONDENSATE

## Slide 85
Pro Series models no longer have physical dipswitches on the circuit board. All programming of the unit is done with the new EZ Start Plus App or the built in operation panel.
EZ START PLUS APP
Directions can be found in the manual

## Slide 86
EZ START PLUS APP
Open EZ Start Plus App and select Contractor
Enter Passcode and tap “NEXT”
Make sure Bluetooth is ON
Select Unit then tap OK

## Slide 87
EZ START PLUS APP
Select Options Based on Installation then tap NEXT
Tap “Unit Setting”
Register Warranty or skip
Tap “Unit Setting”

## Slide 88
EZ START PLUS APP
Upon completion, email app will open to allow emailing the installation settings to Noritz. This is not required, but very helpful for Customer Care.
Please fill out these items if you opt in to send.
Review your selections then tap DONE
App programs unit
Tap OK when complete

## Slide 89
Non-PRO units will have 8 dipswitches located on the circuit board for adjusting the unit based on vent type, elevation, vent length and size.
SETTING THE DIPSWITCHES

## Slide 90
On smaller units that don’t include a remote control, the dipswitches will also allow you to set the output temperature above the default 120 degrees F.
SETTING THE DIPSWITCHES

## Slide 91
Be sure to make dipswitch changes with the power off otherwise an error code 73 will occur.
SETTING THE DIPSWITCHES

## Slide 92
To Clear EC73:
Disconnect Power
Make Dipswitch Changes
Reconnect Power
SETTING THE DIPSWITCHES

## Slide 93
Use the PROCard App to make dipswitch settings simple!
SETTING DIPSWITCHES WITH PROCARD

## Slide 94
Water quality, and specifically hard water, is the #1 factor that affects the lifespan of any water heating appliance.
WATER QUALITY CONSIDERATIONS

## Slide 95
When installing a Noritz Tankless in an area with hard water, it’s important to follow the water quality and treatment guidelines in the installation manual.
WATER QUALITY CONSIDERATIONS

## Slide 96
A Scale Shield is highly recommended for hard water areas. It’s always better to prevent scale build up rather than cleaning it up afterwards.
WATER QUALITY CONSIDERATIONS

## Slide 97
As a last resort if there’s no softener or scale shield, descales should be completed on a yearly basis. This involves circulating a calcium lime rust remover or food grade white vinegar through the unit for 1 hour.
WATER QUALITY CONSIDERATIONS

## Slide 98
All* units since 2016 have a “Flush Mode” used when descaling the unit.
WATER QUALITY CONSIDERATIONS
*NC380-SV Does not have a flush connector.
PRO Series Models
2016+ Models
Directions can be found in the manual

## Slide 99
Descale procedures can be found:
In the Manual
In the PROCard App
SUPPORT.NORITZ.COM
YOUTUBE.COM/NORITZAMERICA
WATER QUALITY CONSIDERATIONS

## Slide 100
Before leaving the jobsite and calling the installation complete, it’s a good practice to verify everything is working properly.
INSTALLATION CHECKLIST

## Slide 101
This includes, but is not limited to:
Double check unit settings
  EZ Start App or Operation Panel for PRO Series
  Dipswitches for other models
Checking inlet water filter
Testing the heater at low, moderate and high flow rates for a few minutes
Registering the warranty
INSTALLATION CHECKLIST

## Slide 102
To keep the tankless running at peak performance and efficiency throughout its life, here are a few other regular maintenance items to keep in mind.
Cleaning the unit and combustion chamber if excessive build up is noticed.
Cleaning the ignition and flame rods.
Checking and cleaning the cold water inlet filter.
REGULAR MAINTENANCE ITEMS

## Slide 103
Encourage your customers to visually check the unit once in awhile.
Tankless heaters, like any other gas appliance, are not meant to be installed and forgotten about.
REGULAR MAINTENANCE ITEMS

## Slide 104
Periodically inspecting the unit for any minor issues will help prevent it from becoming a bigger problem.
REGULAR MAINTENANCE ITEMS

## Slide 105
SUPPORT.NORITZ.COM
NORITZ.COM/TECHTIPS
HELP.NORITZ.COM
TRAINING.NORITZ.COM
YOUTUBE.COM/NORITZAMERICA
Customer Care: 866-766-7489
HELPFUL CONTACT INFO

## Slide 106
THANK YOU